## COVER
UNIVERSITY OF NAMIBIA, HIFIKEPUNYE POHAMBA CAMPUS PROJECT
CONSTRUCT OF A FIRE HYDRANT SYSTEM FOR UNIVERSITY OF NAMIBIA, HIFIKEPUNYE POHAMBA CAMPUS, ONGWEDIVA
PROJECT No.:
CONTRACT No:
CONTRACT NAME:
CONSULTANT: | OM'KUMOH CONSULTING ENGINEERS
CLIENT:
CONTRACTOR: | N/A
DETAIL COST ESTIMATE REPORT FOR THE CONSTRUCTION OF MUNICIPAL SERVICES
DATE
PROJECT OWNERS (CLIENT) |  | PROJECT MANAGERS & ENGINEERS
1

## BOQ-SUMMARY
CONSTRUCT OF A FIRE HYDRANT SYSTEM FOR UNIVERSITY OF NAMIBIA, HIFIKEPUNYE POHAMBA CAMPUS, ONGWEDIVA
Contract Number: |  | 0
BILL OF QUANTITY SUMMARY
Section | Description | Amount N$
1 | PRELIMINARY AND GENERAL
2 | SITE CLEARANCE
3 | MEDIUM-PRESSURE PIPELINES
4 | CLEANING AND FINISHING
NET TOTAL OF TENDER
ADD CONTINGENCIES (10%)
TENDER AMOUNT
ALLOWANCE FOR VAT 15.0%
TOTAL TENDER SUM
| TIME FOR COMPLETION OF CONTRACT (MONTHS) | 8 Months
1

## WATER DESIGN (hidden)
DATE DONE | 2022-05-09
Internal Water Quantities | [9 empty] | Bends | No. | Equal Tees | No. | Cross Tees | No. | SGI Reducing Tees | No. | SGI Hydrant Tees | No. | SGI Reducers | No. | SGI End Caps | No.
[10 empty] | 200 mm diam. 90 deg. | 0 | 250 mm dia |  | 200 mm dia |  | 200 mm x 160 mm dia |  | 75 mm dia |  | 200 mm x 160 mm dia |  | 63 mm dia
Main Pipelines & Fittings | [8 empty] | Total | 200 mm diam. 45 deg. | 0 | 200 mm dia |  | 160 mm dia |  | 200 mm x 110 mm dia |  | 90 mm dia | 36 | 200 mm x 110 mm dia |  | 75 mm dia | 0
Pipe Diameter (Φ) | mm | 200 | 160 | 110 | 90 | 75 | 63 | 50 |  | 200 mm diam. 22,5 deg. | 0 | 160 mm dia | 13 | 110 mm dia | 0 | 160 mm x 110 mm dia | 1 | 110 mm dia |  | 160 mm x 110 mm dia | 0 | 90 mm dia | 36
Pipe length | m | 0 | 4140 | 300 | 1200 | 0 |  |  | 5640 | 200 mm diam. 11,25 deg. | 0 | 110 mm dia | 0 | 90 mm dia | 0 | 160 mm x 90 mm dia | 33 | 160 mm dia |  | 160 mm x 90 mm dia |  | 110 mm dia | 0
Isolating valves | no. | [8 empty] | 160 mm diam. 90 deg. | 2 | 90 mm dia | 0 | 75 mm dia | 0 | 110 mm x 90 mm dia | 1 | 200 mm dia |  | 110 mm x 90 mm dia |  | 160 mm dia | 0
Hydrants | no. | [7 empty] | 0 | 160 mm diam. 120 deg. | 21 | 75 mm dia |  | 63 mm dia |  | 90mm x 75 mm dia | 0 |  |  | 90 mm x 75 mm dia |  | 200 mm dia | 0
Excavation Volume (Manual Calculation) | [9 empty] | 160 mm diam. 22,5 deg. |  | 63 mm dia |  | 50 mm dia |  | 75mm x 63 mm dia |  |  |  | 75 mm x 63 mm dia
Trench width | m | 0.8 | 0.76 | 0.71 | 0.69 | 0.675 | 0.663 | 0.65 |  | 160 mm diam. 11,25 deg.
Bedding | m³ | 0 | 314.64 | 21.3 | 82.8 | 0 | 0 | 0 | 418.74 | 110 mm diam. 90 deg. | 0
Selected fill | m³ | 0 | 1250.6803 | 84.479 | 328.076 | 0 | 0 | 0 | 1663.2353 | 110 mm diam. 45 deg. | 4
General Backfill | m³ | 0 | 1887.84 | 127.8 | 496.8 | 0 | 0 | 0 | 2512.44 | 110 mm diam. 22,5 deg. | 0
Total Excavation Volume | [8 empty] | 4600 | 110 mm diam. 11,25 deg. | 0
[10 empty] | 90 mm diam. 90 deg. | 1
Erf connections |  | Short | Long |  | Civil Designer Output for Excavation |  |  |  |  | 90 mm diam. 45 deg. | 0
Double | no. | 0 | 0 | 0 | Excavation Volume |  |  | Use the Biggest Values |  | 90 mm diam. 22,5 deg. | 0
|  | Short | Long |  | Depth Inc | Volume (m3) |  |  |  | 90 mm diam. 11,25 deg. | 0
Single | no. | 0 | 36 | 36 | 0-0.5 | 0.1 |  |  |  | 75 mm diam. 90 deg. | 0
Total Number of units/Erf Connected |  |  | 36 |  | 0.5-1 | 216.6 |  |  |  | 75 mm diam. 45 deg. | 0
[5 empty] | 1-1.5 | 3551.8 |  |  |  | 75 mm diam. 22,5 deg. | 0
Provisional Allowances |  |  |  |  | 1.5-2 | 446.5 |  |  |  | 75 mm diam. 11,25 deg. | 0
Description |  |  |  | Quantity | 2-2.5 | 5.9 |  |  |  | 63 mm diam. 90 deg.
Extra Over for Excavation |  |  |  | m³ | Total | 4230 |  |  |  | 63 mm diam. 45 deg.
Intermidate Excavation |  |  |  | 460 | Bedding Volume | (m³) |  |  |  | 63 mm diam. 22,5 deg.
Hard Rock Excavation |  |  |  | 4140 | Bedding | 403.6 |  |  |  | 63 mm diam. 11,25 deg. | [5 empty] | FIRE HIDRANTS
Hand excavation in soft material to make connections to existing pipelines (m³) |  |  |  | 20 | Selected Fill | 1308 | [9 empty] | Pipe Size | No. |  |  | Anchor Block
Unsuitable material at trench bottom (8.3.3 C) |  |  |  | 50 | Main Fill | 2455.5 |  |  |  | VALVES | No |  |  |  |  | 250 mm dia |  |  |  | 50mm
Make up Deficiency in backfill material for main fill |  |  |  | 2060 | Total Excavation | 4170 |  |  |  | 50mm dia for 63 & 50mm dia | [5 empty] | 200 mm dia |  |  |  | 63mm | 0
[10 empty] | 80 mm dia for 75mm and 90 mm dia | 7 |  |  |  |  | 160 mm dia |  |  |  | 75mm | 0
[10 empty] | 100 mm dia for 110 mm dia | 2 |  |  |  |  | 110 mm dia |  |  |  | 90mm | 73
| Length | width | Area | [6 empty] | 150 mm dia for 160 mm dia | 41 |  |  |  |  | 90mm dia | 36 |  |  | 110mm | 5
Gravel Wearing course | 10 | 6.4 | 64 | [6 empty] | 200 mm dia for 200 mm dia | [5 empty] | 75 mm dia |  |  |  | 160mm | 70
Asphalt Surfacing | 0 | 6.4 | 0 | [12 empty] | Total no. 0f FH | 0 |  |  | 200mm | 0
65

## Section 1-P&A
Gross
Item Ref | Payment Refers | Bill description | Unit | Bill quantity | Rate | Amount
Section | 1 | PRELIMINARY AND GENERAL
SANS 1200 A
1.1 | 8.3 | Scheduled Fixed-Charge and Value Related Items
1.1.1 | PSA 8.2.1.1 (8.3.1) |  | Sum | 1
PSA 8.2.1.2 (8.3.2)
8.3.2.1
1.1.2 |  | Nameboard | Sum | 1
1.1.7 |  | Living Accomodation | Sum | 1
1.1.8 |  | Ablution and latrine facilities | Sum | 1
1.1.9 |  | Plants,Tools and equipment | Sum | 1
1.1.10 |  | Water supplies, electrical power and communications | Sum | 1
1.1.11 |  | Accomodation of Traffic | Sum | 1 |  | 0
1.1.12 |  | Dealing with Water | Sum | 1 |  | 0
1.1.13 |  | Health and Safety | Sum | 1 |  | 0
1.1.14 |  | Compliance with EMP | Sum | 1 |  | 0
1.1.15 | PSA 8.2.1.1 (8.3.3) | General responsibilities and other fixed charge obligations | Sum | 1 |  | 0
1.1.16 | 8.3.4 | Removal of site establishment | Sum | 1
CARRIED FORWARD
BROUGHT FORWARD
1.2 | 8.4 | Scheduled Time-Related Items
1.2.1 | PSA 8.2.2 (8.4.1) | Contractual requirements | Sum | 1
1.2.2 | PSA 8.2.2 (8.4.2.1) | Operation and maintenance of facilities on site
a) Facilities for Engineer for duration of construction (SABS 1200 AB)
1.2.2 |  | Nameboards | Sum | 1
1.2.3 |  | Survey equipment and assistance | Sum | 1
| PSA 8.2.2 (8.4.2.2) | (b) Facilities for Contractor
1.2.4 |  | Offices and storage sheds | Sum | 1
1.2.5 |  | Workshops | Sum | 1
1.2.6 |  | Laboratory | Sum | 1
1.2.7 |  | Living Accomodation | Sum | 1
1.2.8 |  | Ablution facilities | Sum | 1
1.2.9 |  | Plants, Tools and equipment | Sum | 1 |  | 0
1.2.10 |  | Water supplies, electrical power and communications | Sum | 1 |  | 0
1.2.11 |  | Dealing with Water | Sum | 1 |  | 0
1.2.12 |  | Accommodation of traffic | Sum | 1
1.2.13 |  | Company and head office overhead cost | Sum | 1
1.2.14 | PSA 8.2.2 (8.4.3 to 8.4.5) | General responsibilities and other time related obligations | Sum | 1 |  | 0
1.2.15 |  | Health and Safety | Sum | 1 |  | 0
1.2.16 |  | Compliance with EMP | Sum | 1 |  | 0
CARRIED FORWARD | [5 empty] | 0
BROUGHT FORWARD
1.3 | PSA 8.5 | Sums stated provisionally by the Engineer
Control Testing
1.3.1 |  | (a) Provisional allowance for acceptance testing by the Engineer Representative | Prov Sum | 1
|  | Attendance, charges, etc., on item 1.3.1 | % | 0
1.3.2 |  | Shoring for deep excavation | m²
1.4 | 8.6 | Prime Cost Sums
1.4.1 |  | (i) Additional tests ordered by the Engineer | PC Sum | 1 | 200000
1.4.2 |  | (ii) Charges required by the Contractor on item (i) above | % | 0
1.4.3 |  | (iii) Location, exposure, protection and/or move existing services | PC Sum | 1 | 100000
1.4.4 |  | (iv) Charges required by the Contractor on item (iii) above | % | 0
1.5 | 8.7 | Daywork
Labour (Provisional)
Supply labour including on cost charges
1.5.1 |  | Site foreman | hr | 0 |  | Rate Only
1.5.2 |  | Trade foreman | hr | 0
1.5.3 |  | Artisan | hr | 0
1.5.4 |  | Ganger | hr | 0 |  | Rate Only
1.5.5 |  | Unskilled labourer | hr | 0
Plant (Provisional)
Supply plant incl. operator, fuel, maintenance and pertinent on costs
Bulldozers
|  | 40-60 kW (D4) | hr | 0
1.5.7 |  | 100-120 kW (D6) | hr | 0
1.5.8 |  | Graders (100 kW minimum) | hr | 0
1.5.9 |  | Wheel loaders (50 kW minimum) | hr | 0
Crawler excavators
1.5.10 |  | 60-80 kW | hr | 0
1.5.11 |  | 140-160 kW | hr | 0 |  | Rate Only
1.5.12 |  | Tractor - loader - backhoe | hr | 0 |  | Rate Only
CARRIED FORWARD
BROUGHT FORWARD | [5 empty] | 0
Rollers & Compactors
1.5.13 |  | Pneumatic self propelled rollers (15 ton minimum) | hr | 0 | 397.31 | Rate Only
1.5.14 |  | Smooth self propelled vibra- ting rollers (7 ton minimum) | hr | 0 | 640.6 | Rate Only
1.5.15 |  | Plate compactors | hr | 0 | 28.75 | Rate Only
Trucks
1.5.16 |  | Tip truck (10 m3 minimum) | hr | 0 | 530.6 | Rate Only
1.5.17 |  | Tip truck (5 m3 minimum) | hr | 1 | 336.51 | Rate Only
1.5.18 |  | Water truck (9 kl minimum) | hr | 0 | 673.5 | Rate Only
1.5.19 |  | 1 Ton LDV | hr | 0 | 80 | Rate Only
1.5.20 |  | Compressor including hammers & hoses (5 m3/min minimum) | hr | 0 | 215.84 | Rate Only
Centrifugal Pumps
1.5.21 |  | 50 mm | hr | 0 | 30.79 | Rate Only
1.5.22 |  | 100 mm | hr | 0 | 43.98 | Rate Only
1.6 | 8.8 | Temporary Works
1.6.1 | 8.8.3 | Protect existing structure/s until construction in vicinity complete | Sum | 1 |  | 0
TOTAL CARRIED TO SUMMARY | [5 empty] | 0

## Section 2 Site Clearance
Gross
Item Ref | Payment Refers | Bill description | Unit | Bill quantity | Rate | Amount
Section | 2 | SITE CLEARANCE
| SANS 1200 D | SITE CLEARANCE
Clear and Grub Site
2.1 |  | Water Reticulation
2.1.1 | PSC 8.2.1 | Clear vegetation and boulder stones including trees of girth up to 1m within the pipeline routes not falling into road reserves to a width of 1,5m from centre line and remove all unsuitable to Municipal spoil site or as instructed by the Engineer | m | 5640
2.1.2 | PSC 8.2.2 | Clear trees of girth between 1m to 3m, in roadways, cut trunks into lengths of 1.5m, remove trunk sections to stockpile and remove remaining material to designated spoil sites | sum
TOTAL CARRIED TO SUMMARY
1
Note on C60: Menelik Negussie: Tarred Road
Note on F64: Menelik Negussie: 5% Stabilise

## Section 3-Water
Gross
Item Ref | Payment Refers | Bill description | Unit | Bill quantity | Rate | Amount
Section | 3 | MEDIUM-PRESSURE PIPELINES
3.1 | SANS 1200 DB | Excavation and Backfilling
3.1.1 | SANSDB 8.3.2 | (a) Excavate in all materials for trenches, backfill, compact and dispose of surplus/unsuitable material to approved dump site as instructed by the Engineer for:
3.1.1.1 |  | Pipes smaller and equal to 200 mm dia and depth exceeding 1,0m but not exceeding 1,5m | m | 5640
3.1.2 |  | (b) Extra-over item (3.1.1) above for:
3.1.2.1 |  | (i) Intermediate excavation | m³
3.1.2.3 |  | (ii) Hand excavation in soft material to make connections to existing pipelines | m3 | 20
3.1.3.2 |  | (b) by importation from designated borrow pit | m³ | 1648
3.1.3.3 |  | c) from importation from designated borrow pit / commercial or off-site sources selected by Contractor | m³ | 412
3.1.4 | 8.3.6 | Finishing Reinstate road surfaces complete with all courses
|  | (a) Gravel wearing course roads | m³ | 64
3.1.4.1 |  | (b) Cape Seal wearing course (Double Seal) | m2 | 0 |  | Rate only
CARRIED FORWARD | [5 empty] | 0
BROUGHT FORWARD | [5 empty] | 0
3.2 | SABS 1200 LB | Provision of Bedding
Construct Class C Bedding Cradle to 93% Mod AASHTO Density from:
| SANS LB 8.2.2.1 | Available from other necessary excavations on site within 0,5 km :
3.2.1 |  | a) Selected granular material | m³ | 0
3.2.2 |  | b) Selected fill material | m³ | 0
Imported from
| SANS LB 8.2.2.3 | b) From borrow pits (Provisional) on instruction
3.2.3 |  | 1) Selected granular material | m³ | 314.055
3.2.4 |  | 2) Selected fill material | m³ | 1250
| SANS LB 8.2.2.3 | c) Commercial sources (Provisional) on instruction
3.2.5 |  | 1) Selected granular material | m³ | 110
3.2.6 |  | 2) Selected fill material | m³ | 420
3.3 | SABS 1200 L | Pipeline
| 8.2.1 | Supply, lay, joint, bed as class C, test and disinfect Class 12 uPVC pipes to SABS 966 with O-ring joints
3.3.2 |  | 160 mm dia | m | 4140
3.3.3 |  | 110 mm dia | m | 300
3.3.4 |  | 90 mm dia | m | 1200
3.4 | SABS 1200 L | Specials and Fittings for uPVC Pipes - Class 12 complete with couplings for:
| 8.2.2 | Supply, lay, joint, bed, cut pipes, test and disinfect extra-over item 3.3 for pipework
Bends
3.4.5 |  | 160 mm diam. 90 deg. | No | 2
3.4.6 |  | 160 mm diam. 120 deg. | No | 21
3.4.13 |  | 90 mm diam. 90 deg. | No | 1 |  | 0
CARRIED FORWARD | [5 empty] | 0
BROUGHT FORWARD | [5 empty] | 0
Equal Tees (Plain-ended)
3.4.27 |  | 160 mm dia | No | 13
SGI Reducing Tees
3.4.38 |  | 160 mm x 110 mm dia | No | 1
3.4.39 |  | 160 mm x 90 mm dia | No | 33
3.4.40 |  | 110 mm x 90 mm dia | No | 1
SGI Hydrant Tees
3.4.44 |  | 90 mm dia | No | 36
SGI Reducers: Male/Female reducer (spigot & socket)
3.4.57 |  | 90 mm dia | No | 36
3.5 | 8.2.3 | Valves
3.5.1 |  | 80 mm dia for 75 & 90 mm dia uPVC | No | 7
3.5.2 |  | 100 mm dia for 110 mm dia uPVC | No | 2
3.5.3 |  | 150 mm dia for 160 mm dia uPVC | No | 41
3.5.7 |  | 150mm Non-return Valve to SANS | No | 1
3.6 |  | Hydrants
3.6.1 |  | 80mm Woodlands right angled tamperproof Fire Hydrant with instataneous single lug outlet (WTS80) complete with 80 mm extension pipe one end flanged one end threaded and 80 mm flanged extension piece as per drawing | No | 36
3.6.2 |  | Extra-over 3.6.1 for encasing joints (Denso wrapping) | No | 36
3.7 |  | Ancillaries
| 8.2.11 | Anchor/thrust blocks and pedestals as per detail drawing (Concrete class 20 Mpa) ,to be cast into open trench and against undisturbed soil, inclusive of formwork as required:
3.7.3 |  | 90 mm dia fittings | No | 73
3.7.4 |  | 110 mm dia fittings | No | 1
3.7.5 |  | 160 mm dia fittings | No | 71
3.8 |  | Valve Chambers and Manholes
| 8.2.13 | Construct Valve / Hydrant Chambers complete as per the typical drwaings
3.8.1 |  | a) Valve chambers to SANS drawing L-1 (Refer to Typical Drawings) | No | 51
3.8.2 |  | b) Hydrant chambers to SANS drawing L-2 (Refer to Typical Drawings) | No | 36
3.8.3 |  | c) Air valve chambers to Typical Drawing | No | 2
3.10 |  | Connection to Exisitng Mains
Connections to the existing main including excavations, cutting in, local authority liaison, connecting and making good to the satisfaction of the Engineer;
3.10.1 |  | a) 150mm dia | No. | 1
TOTAL CARRIED TO SUMMARY | [5 empty] | 0

## Section 4-CLEANING
Gross
Item Ref | Payment Refers | Bill description | Unit | Bill quantity | Rate | Amount
Section | 4 | CLEANING AND FINISHING
4.1 |  | Cleaning and finishing of site after completion of the works and the removal of all construction rubble and debris to approved spoil sites | Sum | 1 |  | 0
TOTAL CARRIED TO SUMMARY
1